## Table 1
Residential Electric Load Calculations
Please submit a separate Electric Load Calculations Form for Main House and ADU
Property Address:
Total Square Feet of Living Space: |  | Check One: | FALSE | Main House |  |  | FALSE | ADU | ** Fill in colored cells**
Existing Panel Rating Amp: |  | Check One: | FALSE | Main Service Panel |  |  | FALSE | Subpanel
General Lighting |  |  | Quantity |  |  |  | Volt Amperes (VA)
1. General Lighting (Sq. Ft. x 3 VA per Sq. Ft.) CEC 220.41 |  |  | 3 x |  | 0 | Sq. Ft | 0
2. Small Appliance Circuits: 2 minimum (1500 VA per circuit) CEC 220.52(A) |  |  | 1500 x |  |  |  | 0
3. Laundry Circuit (1500 VA per circuit) CEC 220.52(B) |  |  | 1500 x |  |  |  | 0
4. Total General Lighting Load (Add lines 1, 2 & 3) | [6 empty] | 0
5. First 3000 VA of General Lighting Load @ 100% | [6 empty] | 0
6. Total General Lighting Load (Total from Line #4 - 3000) = |  | 0 | @ 35% (multiply by 0.35) |  |  |  | 0
7. Net General Lighting Load (Add Lines #5 & 6) CEC 220.45 | [6 empty] | 0
Fixed Appliances | Volt Amperes (VA) Each |  | Quantity |  |  |  | Volt Amperes (VA)
Garbage Disposal (min 800 VA) | [6 empty] | 0
Microwave (min 1000 VA) | [6 empty] | 0
Dishwasher (min 1200 VA) | [6 empty] | 0
Compactor (min 1000 VA) | [6 empty] | 0
Freezer (min 1200VA) | [6 empty] | 0
Swimming Pool (min 1000 VA) | [6 empty] | 0
Other: | [6 empty] | 0
Other: | [6 empty] | 0
|  | TOTALS: | 0 |  |  |  | 0
8. If there are 3 or less Fixed Appliances, enter the Total Fixed Appliance VA; If there are 4 or more Fixed Appliances, enter 75% of Total Fixed Appliance VA (CEC 220.53): |  |  |  | Total Fixed Appliance VA= |  |  | 0
Other Loads | Nameplate rating: Volt Amperes (VA) Each |  | Quantity |  |  |  | Volt Amperes (VA)
9. Air Conditioner (min 1600 VA per ton) | [6 empty] | 0
10. Heater (min 550 VA ) | [6 empty] | 0
11. Electric Clothes Dryer (min 5500 VA) | [6 empty] | 0
12. Electric Range (min 12,000 VA) | [6 empty] | 0
13. Electric Oven (min 8000 VA) | [6 empty] | 0
14. Electric Vehicle Charger | [6 empty] | 0
15. Heat Pump Water Heater (min 5000 VA) | [6 empty] | 0
16. Other: | [6 empty] | 0
17. Other: | [6 empty] | 0
18. 25% of largest motor (CEC 430.24) | 0
19. Total "Other Loads": (Add lines #9-18) | [6 empty] | 0
Total Service Load Volt Amperes: (Add Lines #7, 8, 19) | [6 empty] | 0
Convert to Amps. Divide "Total Service Load VA" by 240 volts. (Total service load VA divide 240) | [6 empty] | 0
AMP Service Rating must be equal to or greater than the existing Main Service Panel VA, but in no case less than 100 AMPS (CEC 225.39 & 230.79)